## PlatformTypes
PlatformType | subClassOf_PlatformType
EVCharger | Consumer
Battery | Buffer
PVSystem | Producer
Garage | EnvelopeEntity

## SensorTypes
SensorType | subClassOf_SensorType
AP_EVCharger_Sensor | AP_Sensor
AP_AllEVChargers_Sensors | AP_Sensor
AP_Battery_Sensor | AP_Sensor
SOC_Battery_Sensor | SOC_Sensor
AP_PVSystem_Sensor | AP_Sensor
AP_Garage_Sensor | AP_Sensor
OE_Garage_Sensor | OE_Sensor
EnvelopeViolation_Garage_Sensor | EnvelopeViolation_Sensor
AP_Sensor | Sensor
SOC_Sensor | Sensor
OE_Sensor | Sensor
EnvelopeViolation_Sensor | Sensor

## 1_StateTypes
StateType | SensorType_possible | TriggerExplanation_State | Description
BatteryDip_State | AP_Battery_Sensor | FALSE | Low AP from Battery for a small time frame
BatteryDischargeDifference_State | AP_Battery_Sensor | FALSE | Battery AP is continually increasing
BatteryUnused_State | AP_Battery_Sensor | FALSE | Battery is not charging or discharging
BatteryDischarging_State | AP_Battery_Sensor | FALSE | Battery is discharging | not used currently
BatteryCharging_State | AP_Battery_Sensor | FALSE | battery is charging | not used currently
BatteryLowSOC_State | SOC_Battery_Sensor | FALSE | Battery SOC is below a threshold (e.g.15%)
BatteryHighSOC_State | SOC_Battery_Sensor | FALSE | Battery SOC is above a certain thrshold (e.g.95%) | not used currently
EVIndividualHighCharging_State | AP_EVCharger_Sensor | FALSE | AP of charging of a single EV Charger is higher than the envelope
EVIndividualChargingDifference_State | AP_EVCharger_Sensor | FALSE | Rapid increase in the charging of this evcharger / gradient Increase of AP of EV
EVOverallHighCharging_State | AP_AllEVChargers_Sensors | FALSE | AP of charging of all EV Chargers in total is higher than the envelope
EVOverallChargingDifference_State | AP_AllEVChargers_Sensors | FALSE | Rapid increase in the charging of an evcharger somewhere
DemandEnvelopeViolation_State | EnvelopeViolation_Garage_Sensor | TRUE | Violation Sensor Value is above 0/ AP of Garage is higher than envelope value
InfeedEnvelopeViolation_State | EnvelopeViolation_Garage_Sensor | TRUE | AP of Garage infeed is lower than envelope value | not used currently
Note on C1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: every other states has be connected to starter state through some causal relations (can be indirect) Reply: this is important to mark the first step in the method.

## 1_StateTypeCausality
Number | StateType_cause | causalRelation | temporalRelation | topologicalRelation | StateType_effect | Justification/Description
1 | EVOverallHighCharging_State | causes | overlaps | parentPlatform | DemandEnvelopeViolation_State
3.1 | EVOverallHighCharging_State | causes | before | siblingPlatform | BatteryLowSOC_State
1.1 | EVIndividualHighCharging_State | causes | overlaps | parentPlatform | EVOverallHighCharging_State
2 | BatteryDip_State | enables | overlaps | parentPlatform | DemandEnvelopeViolation_State
3 | BatteryLowSOC_State | enables | overlaps | parentPlatform | DemandEnvelopeViolation_State | maybe not include, as it is included via batteryUnused
4 | BatteryDischargeDifference_State | enables | overlaps | parentPlatform | DemandEnvelopeViolation_State
4.1 | EVOverallChargingDifference_State | causes | overlaps | siblingPlatform | BatteryDischargeDifference_State
4.1.1 | EVIndividualChargingDifference_State | causes | overlaps | parentPlatform | EVOverallChargingDifference_State
5 | BatteryUnused_State | enables | overlaps | parentPlatform | DemandEnvelopeViolation_State
5.1 | BatteryLowSOC_State | causes | overlaps | samePlatform | BatteryUnused_State | do we need to extend this to battery not discharging?
Note on F1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: this needs to be extended by @muhammad.bilal@tuwien.ac.at

## 2_EventStateMapping
EventType | StateType_starts | StateType_ends | Event Detection Rule Description | Implementation Formalism
DemandEnvelopeViolated_Event | DemandEnvelopeViolation_State |  | AP Garage > Envelope Garage | STL
DemandEnvelopeNormal_Event |  | DemandEnvelopeViolation_State | AP Garage <= Envelope Garage | STL
EVOverallHighCharging_Event | EVOverallHighCharging_State |  | AP OverallEVs > Envelope Garage
EVOverallNormalCharging_Event |  | EVOverallHighCharging_State | AP OverallEVs <= Envelope Garage
EVIndividualHighCharging_Event | EVIndividualHighCharging_State |  | AP Indiviual EV > Envelope Garage
EVIndividualNormalCharging_Event |  | EVIndividualHighCharging_State | AP Individual EV <= Envelope Garage
EVOverallHighChargingDifferenceStarted_Event | EVOverallChargingDifference_State |  | First Derivative of AP Overall EVs > THRESHOLD & second derivative >0 |  | to be defined by siemens
EVOverallHighChargingDifferenceEnded_Event |  | EVOverallChargingDifference_State | First Derivative of AP Overall EVs <= THRESHOLD |  | to be defined by siemens
EVIndividualHighChargingDifferenceStarted_Event | EVIndividualChargingDifference_State |  | First Derivative of AP single EVs > THRESHOLD |  | to be defined by siemens
EVIndividualHighChargingDifferenceEnded_Event |  | EVIndividualChargingDifference_State | First Derivative of AP single EVs <= THRESHOLD |  | to be defined by siemens
BatteryNotUsed_Event | BatteryUnused_State | BatteryCharging_State | Battery AP = 0, consider margin
BatteryNotUsed_Event |  | BatteryDischarging_State
BatteryCharging_Event | BatteryCharging_State | BatteryDischarging_State | Battery AP < 0, consider margin
BatteryCharging_Event |  | BatteryUnused_State
BatteryDischarging_Event | BatteryDischarging_State | BatteryCharging_State | Battery AP > 0, consider margin
BatteryDischarging_Event |  | BatteryUnused_State
BatterySocLow_Event | BatteryLowSOC_State |  | SoC < 15% ( THRESHOLD)
BatterySocNotLow_Event |  | BatteryLowSOC_State | SoC >= 15% ( THRESHOLD)
BatteryAPDropped_Event | BatteryDip_State |  | BatteryAP at t-1 > at t (THRESHOLD)
BatteryAPBackToNormal_Event |  | BatteryDip_State | BatteryAP at t-1 < at t (THRESHOLD) + dropped before
BatteryDischargeDifferenceStarted_Event | BatteryDischargeDifference_State |  |  |  | to be defined by siemens
BatteryDischargeDifferenceEnded_Event |  | BatteryDischargeDifference_State |  |  | to be defined by siemens
Note on A1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Priorities Prio1 Prio2 Prio3 Prio4
Note on D1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @TU: please check and extend if necessary

## Sensors
Sensor | SensorType | hostedBy_Platform | observes_ObservableProperty | TimeseriesId
AP_Garage1_Sensor | AP_Garage_Sensor | Garage1 | ActivePower
OE_Garage1_Sensor | OE_Garage_Sensor | Garage1 | OperatingEnvelope | measurement=seehub,field=LEM.SCC.Peakshave_Sollwert_refl
AP_AllEVChargers1_Sensor | AP_AllEVChargers_Sensors | AllEVChargers1 | ActivePower
EnvelopeViolation_Garage1_Sensor | EnvelopeViolation_Garage_Sensor | Garage1 | EnvelopeViolation
AP_EVChargerDelta1_Sensor | AP_EVCharger_Sensor | EVChargerDelta1 | ActivePower | measurement=seehub,field=LEM.Delta_Wallbox.Wirkleistung_P
AP_EVChargerKeba1_Sensor | AP_EVCharger_Sensor | EVChargerKeba1 | ActivePower | measurement=seehub,field=LEM.KEBA_P30_1.Wirkleistung_P
AP_EVChargerKeba2_Sensor | AP_EVCharger_Sensor | EVChargerKeba2 | ActivePower | measurement=seehub,field=LEM.KEBA_P30_2.Wirkleistung_P
AP_EVChargerKeba3_Sensor | AP_EVCharger_Sensor | EVChargerKeba3 | ActivePower | measurement=seehub,field=LEM.KEBA_P30_3.Wirkleistung_P
AP_EVCharger1_Sensor | AP_EVCharger_Sensor | EVCharger1 | ActivePower | measurement=seehub,field=LEM.Ladebox1.P
AP_EVCharger2_Sensor | AP_EVCharger_Sensor | EVCharger2 | ActivePower | measurement=seehub,field=LEM.Ladebox2.P
AP_EVCharger3_Sensor | AP_EVCharger_Sensor | EVCharger3 | ActivePower | measurement=seehub,field=LEM.Ladebox3.P
AP_EVChargerSiCharge1_Sensor | AP_EVCharger_Sensor | EVChargerSiCharge1 | ActivePower | measurement=seehub,field=LEM.SICHARGE_D.Wirkleistung_P
AP_Battery1_Sensor | AP_Battery_Sensor | Battery1 | ActivePower
SOC_Battery1_Sensor | SOC_Battery_Sensor | Battery1 | StateOfCharge
AP_Battery2_Sensor | AP_Battery_Sensor | Battery2 | ActivePower
SOC_Battery2_Sensor | SOC_Battery_Sensor | Battery2 | StateOfCharge
AP_BatteryOverview_Sensor | AP_Battery_Sensor | BatteryOverview | ActivePower | measurement=seehub,field=LEM.Overview.Wirkleistung_P
SOC_BatteryOverview_Sensor | SOC_Battery_Sensor | BatteryOverview | StateOfCharge | measurement=seehub,field=LEM.Overview.Battery_SOC
AP_PVSystem1_Sensor | AP_PVSystem_Sensor | PVSystem1 | ActivePower | measurement=seehub,field=LEM.PV_Anlage.Wirkleistung_P

## Platforms
Platform | PlatformType | hostedBy_Platform
Garage1 | Garage | System
EVChargerDelta1 | EVCharger | AllEVChargers1
EVChargerKeba1 | EVCharger | AllEVChargers1
EVChargerKeba2 | EVCharger | AllEVChargers1
EVChargerKeba3 | EVCharger | AllEVChargers1
EVCharger1 | EVCharger | AllEVChargers1
EVCharger2 | EVCharger | AllEVChargers1
EVCharger3 | EVCharger | AllEVChargers1
EVChargerSiCharge1 | EVCharger | AllEVChargers1
Battery1 | Battery | BatteryOverview
Battery2 | Battery | BatteryOverview
BatteryOverview | Battery | Garage1
PVSystem1 | PVSystem | Garage1
AllEVChargers1 | EVCharger | Garage1